## 1 Isolated (MACC)
ref | name | theme | category | class | confidence | capex_central_£ | capex_low_£ | capex_high_£ | annual_elec_kWh | annual_gas_kWh | annual_£_saving | EUI_Δ_kWh_m2 | lifetime_tCO2e | £_per_tCO2e | simple_payback_yr | flags | basis
3.3 | Setpoint optimisation (heating/cooling dead-band) | Heating & cooling | Controls | A | H | 0 | 0 | 500 | 13084 | 0 | 3664 | -3.1 | 8.4 | 0 | 0 | EP-validated ✓ | Heating 21→20, cooling 24→25 (doc example). Widened dead-band within comfort agreement.
1.1 | Reduce DHW demand (low-flow fittings) | Hot water | Systems (water) | A | M | 8280 | 5520 | 13800 | 8011 | 30627 | 4387 | -9.2 | 89.7 | 92 | 1.9 | EP-validated ✓ | DHW demand −19.5%: shower fraction 65% (mid 60–70%) × low-flow volume reduction 30% (aerator/regulator standard). Within the doc's −10..−25% band.
1.4 | Larger ASHP — full DHW off gas | Hot water | Systems | A | M | 105000 | 80000 | 140000 | -47562 | 157428 | -2297 | -26 | 399.3 | 263 |  | EP-validated ✓ | Gas DHW off (share 0), ASHP serves 100% at high-temp SCOP 2.9 (mid 2.8–3.0). The principal carbon measure (gas→electric).
1.2 | Waste-water heat recovery (WWHR) | Hot water | Systems | B | L | 22000 | 15000 | 35000 | 7412 | 28337 | 4059 | -8.5 | 83 | 265 | 5.4 | EP-validated ✓ allowance-only | Design note: DHW demand scalar 0.82 (shower 65% × HX effectiveness 45% × config factor 0.6 ≈ −18%). Modelled as demand-litres ×0.82 (55→45.1). SAME PATH as 1.1 — see cumulative caveat.
2.2 | Reduce fan duty | Ventilation | Systems/controls | A | M | 2600 | 1500 | 5000 | 15101 | 0 | 4228 | -3.6 | 9.7 | 268 | 0.6 | EP-validated ✓ | Bedroom extract flow 2208→1590 (−28%, per doc's 2292→1656 case). Fan power falls with the cube law → SFP scaled by (flow ratio)² (0.9→0.47) so fan energy ∝ flow³.
4.2 | Automatic room shut-off (keycard/occupancy master switch) | Room loads | Occupancy | A | M | 19320 | 11000 | 28000 | 45631 | 0 | 12777 | -10.8 | 29.4 | 657 | 1.5 | EP-validated ✓ | Room plug load −25% (mid of doc's −20..−30% when unoccupied). Equipment baseload 5.04→3.78 W/m² (net occupancy-weighted).
1.3 | Exhaust air over ASHP (COP uplift) | Hot water | Systems | B | L | 4550 | 3050 | 8550 | 4844 | 0 | 1356 | -1.1 | 3.4 | 1338 | 3.4 | EP-validated ✓ allowance-only | Design note: preheat-stage COP +0.4 absolute (3.0→3.4), applies to the ASHP preheat share of DHW (dhw[1], 48%). SAME PATH as 1.4 — see cumulative caveat.
3.1 | VRF metering, commissioning & diagnostic health check | Heating & cooling | Systems/controls | B | M | 8100 | 5000 | 12000 | 7233 | 0 | 2025 | -1.7 | 4.7 | 1723 | 4 | EP-validated ✓ | Design note sensitivity band: none / central +0.4 / strong (managed 3.9). CENTRAL (+0.4 on in-service VRF heating SCOP + cooling EER, 3.0→3.4) is the stack member; none/strong stored as sensitivity. SAME PATH as 3.2 — 3.2 composes on the post-3.1 state.
1.5 | Interlinked heat recovery — VRF→DHW | Hot water | Systems | C | L | 25000 | 15000 | 35000 | 20622 | 0 | 5774 | -4.89 | 14.4 | 1736 | 4.3 | allowance-only off-model | Off-model (Class C): monthly-coincidence calc, 55% capture. Neither engine models inter-plant heat flows.
7.1 | Solar PV | Carbon | Other | C | H | 55000 | 35000 | 55000 | 40375 | 0 | 11305 | 0 | 30.8 | 1786 | 4.9 | off-model | Off-model (Class C): 50 kWp × 950 kWh/kWp = 47.5 MWh/yr, 85% self-consumption; EUI UNCHANGED by construction (CRREM gross-demand rule). Carbon valued on the declining grid pathway.
3.4 | Fabric — glazing G-value (solar film) | Heating & cooling | Fabric | A | M | 8685 | 5000 | 14000 | 4434 | 0 | 1242 | -1 | 3.4 | 2554 | 7 | EP-validated ✓ | Glazing g 0.55→0.42 (nearest library construction double_low_e; u unchanged at 1.4 — film reduces g, not u; doc target g 0.40). Expected marginal/counterproductive here (cuts useful winter heat, raises cooling). Film life ~10–15y in reality but note maps fabric→30y.
3.2 | VRF replacement (current-gen R-32 heat recovery) | Heating & cooling | Systems | B | M | 375000 | 280000 | 480000 | 12295 | 0 | 3443 | -2.9 | 79.8 | 4699 | 108.9 | EP-validated ✓ | Heating/cooling consumption −20% (spec 15–25%), via rated-SCOP substitution derated to in-service: eff 3.0→3.75 (=3.0/0.8). CUMULATIVE: computed against the post-3.1 state (3.4→4.25) per the note's double-count guard. Plus Class C refrigerant carbon ≈4.7 tCO₂e/yr (offmodel).
5.2 | Communal lighting + controls | Communal | Lighting | A | M | 20100 | 12000 | 30000 | 5695 | 0 | 1595 | -1.3 | 4 | 5025 | 12.6 | EP-validated ✓ | Whole-building lighting magnitude −15% (2.0→1.7 W/m²) representing communal LED + PIR occupancy sensing on the communal fraction. [15% is a stated assumption — communal share × PIR saving.]
3.5 | Brise soleil (external solar shading) | Heating & cooling | Fabric | A | M | 23100 | 17000 | 34000 | 530 | 0 | 148 | -0.1 | 0.4 | 57750 | 156.1 | EP-validated ✓ | 0.5 m horizontal overhang on the SW/S/W-facing glazing → modelled as south + west facades of the 4-orientation box (North_Axis 42). Seasonally selective (cuts summer sun, admits winter).
2.1 | MVHR replacing central electric heating + bathroom extract | Ventilation | Systems | A | L | 99000 | 70000 | 140000 | -19784 | 0 | -5540 | 4.7 | -13.8 |  |  | EP-validated ✓ allowance-only | Bedroom extract → balanced MVHR 80% HR, SFP 1.8 (mid 1.5–2.0). Electric panel heating (heating[1], 5%) removed → VRF 100%. Note: net effect may be adverse (summer) — modelling decides.
2.3 | Heat-recovery bypass setpoint | Ventilation | Controls | A | H | 0 | 0 | 500 | [7 empty] | off-model no-model | NO clean static-engine representation — seasonal HRV bypass is a control the static engine does not expose (no seasonal-recovery field). Modelled effect ≈ 0; a near-free control with a small summer cooling benefit not captured. Cost within 6.1.
4.1 | Room load monitoring (sample sub-metering) | Room loads | Occupancy (enabling) | D | M | 4500 | 3000 | 8000 | [7 empty] | enabling | Enabling: no demand change; converts assumed room load into data. Sizes 4.2.
4.3 | Equipment efficiency at replacement | Room loads | Other | D | H | 0 | 0 | 0 | [7 empty] | enabling | £0 capex by definition (efficient spec at natural replacement). No energy claim modelled.
5.1 | Kitchen/catering review + circuit metering | Communal | Other (enabling) | D | M | 2300 | 1500 | 4000 | [7 empty] | enabling | Enabling: quantum unknown by design; no modelled demand change.
5.3 | Building sub-metering package (plant + water) | Communal | Other (enabling) | D | M | 13300 | 9000 | 20000 | [7 empty] | enabling | THE enabling measure: no demand change; resolves the report's largest unknown. First action overall.
5.4 | Communal ventilation run-hours | Communal | Controls | D | H | 0 | 0 | 500 | [7 empty] | enabling | Within the 6.1 controls visit. Align HRV schedules to space use; small saving not separately modelled (within 6.1 / not a headline claim).
6.1 | BMS setpoint realignment + schedules (consolidated controls visit) | Controls & BMS | Controls | D | H | 3000 | 2000 | 6000 | [7 empty] | enabling | Cost-carrier for the settings measures (3.3, 5.4, 2.3). Their energy savings are claimed under those refs; 6.1 carries the £3,000 visit so the settings measures read £0 capex (avoids double-count).

## 2 Cumulative (spine)
step | ref | name | class | cumulative_capex_£ | cumulative_EUI_kWh_m2 | cumulative_annual_£_saving | cumulative_lifetime_tCO2e | EUI_vs_CRREM_2026 | EUI_vs_plateau_95 | note
1 | 5.3 | Building sub-metering package (plant + water) | D | 13300 | 126 | 0 | 0 | -58.1 | 31 | enabling (£0 energy)
2 | 4.1 | Room load monitoring (sample sub-metering) | D | 17800 | 126 | 0 | 0 | -58.1 | 31 | enabling (£0 energy)
3 | 5.1 | Kitchen/catering review + circuit metering | D | 20100 | 126 | 0 | 0 | -58.1 | 31 | enabling (£0 energy)
4 | 6.1 | BMS setpoint realignment + schedules (consolidated controls visit) | D | 23100 | 126 | 0 | 0 | -58.1 | 31 | enabling (£0 energy)
5 | 3.3 | Setpoint optimisation (heating/cooling dead-band) | A | 23100 | 122.9 | 3664 | 8.4 | -61.2 | 27.9
6 | 5.4 | Communal ventilation run-hours | D | 23100 | 122.9 | 3664 | 8.4 | -61.2 | 27.9 | enabling (£0 energy)
7 | 2.3 | Heat-recovery bypass setpoint | A | 23100 | 122.9 | 3664 | 8.4 | -61.2 | 27.9
8 | 2.2 | Reduce fan duty | A | 25700 | 119.7 | 7430 | 17.1 | -64.4 | 24.7
9 | 3.1 | VRF metering, commissioning & diagnostic health check | B | 33800 | 118.4 | 9021 | 20.8 | -65.7 | 23.4
10 | 1.1 | Reduce DHW demand (low-flow fittings) | A | 42080 | 109.2 | 13408 | 110.5 | -74.9 | 14.2
11 | 5.2 | Communal lighting + controls | A | 62180 | 107.8 | 15094 | 114.7 | -76.3 | 12.8
12 | 4.2 | Automatic room shut-off (keycard/occupancy master switch) | A | 81500 | 96.5 | 28383 | 145.3 | -87.6 | 1.5
13 | 4.3 | Equipment efficiency at replacement | D | 81500 | 96.5 | 28383 | 145.3 | -87.6 | 1.5 | enabling (£0 energy)
14 | 3.2 | VRF replacement (current-gen R-32 heat recovery) | B | 456500 | 94.6 | 30658 | 222.2 | -89.5 | -0.4 | incl. refrigerant carbon
15 | 1.5 | Interlinked heat recovery — VRF→DHW | C | 481500 | 89.7 | 36432 | 236.6 | -94.4 | -5.3 | off-model
16 | 1.4 | Larger ASHP — full DHW off gas | A | 586500 | 73.6 | 34581 | 558.2 | -110.5 | -21.4
17 | 1.2 | Waste-water heat recovery (WWHR) | B | 608500 | 73.9 | 34220 | 557.3 | -110.2 | -21.1
18 | 1.3 | Exhaust air over ASHP (COP uplift) | B | 613050 | 71.4 | 37216 | 564.8 | -112.7 | -23.6
19 | 7.1 | Solar PV | C | 668050 | 71.4 | 48521 | 595.6 | -112.7 | -23.6 | off-model
20 | 3.4 | Fabric — glazing G-value (solar film) | A | 676735 | 70.6 | 49383 | 597.9 | -113.5 | -24.4
21 | 3.5 | Brise soleil (external solar shading) | A | 699835 | 70.6 | 49432 | 598.1 | -113.5 | -24.4
22 | 2.1 | MVHR replacing central electric heating + bathroom extract | A | 798835 | 74.8 | 44516 | 585.8 | -109.3 | -20.2

## 3 EP validation
ref | name | status | EUI_NZA_Δ | EUI_EP_Δ | EUI_Δ% | heating_NZA_Δ | heating_EP_Δ | heating_Δ% | cooling_NZA_Δ | cooling_EP_Δ | cooling_Δ%
1.1 | Reduce DHW demand (low-flow fittings) | done | -9.2 | -7.3 | 21 | 0 | 0 |  | 0 | 0
1.2 | Waste-water heat recovery (WWHR) | done | -8.5 | -6.8 | 20 | 0 | 0 |  | 0 | 0
1.3 | Exhaust air over ASHP (COP uplift) | done | -1.1 | -0.9 | 18 | 0 | 0 |  | 0 | 0
1.4 | Larger ASHP — full DHW off gas | done | -26 | -20.8 | 20 | 0 | 0 |  | 0 | 0
2.1 | MVHR replacing central electric heating + bathroom extract | done | 4.7 | 4.4 | -6 | -84.3 | -95.5 | -13 | 100.2 | 160 | 60
2.2 | Reduce fan duty | done | -3.6 | -1.5 | 58 | -37.2 | -41.1 | -10 | 28.2 | 26.5 | -6
3.1 | VRF metering, commissioning & diagnostic health check | done | -1.7 | -2 | -18 | 0 | 0 |  | 0 | 0
3.2 | VRF replacement (current-gen R-32 heat recovery) | done | -2.9 | -3.5 | -21 | 0 | 0 |  | 0 | 0
3.3 | Setpoint optimisation (heating/cooling dead-band) | done | -3.1 | -1.8 | 42 | -18.6 | -16.8 | 10 | -18.9 | -4.4 | 77
3.4 | Fabric — glazing G-value (solar film) | done | -1 | -1.6 | -60 | 8 | 3.1 | -61 | -22.1 | -24 | -9
3.5 | Brise soleil (external solar shading) | done | -0.1 | -0.5 | -400 | 2.1 | 0.5 | -76 | -3.9 | -7 | -79
4.2 | Automatic room shut-off (keycard/occupancy master switch) | done | -10.8 | -10.7 | 1 | 20.1 | 21 | 4 | -19.4 | -19 | 2
5.2 | Communal lighting + controls | done | -1.3 | -1.6 | -23 | 2.7 | 2.5 | -7 | -2.5 | -2.8 | -12