## 00_README
Bridgewater bottom-up energy model
Purpose
Bottom-up calculation of Bridgewater's annual energy use, system by system, against standard convention.
Bottom-up means no reverse-engineering from gas bills. Measured energy used only as a validation comparison.
Methodology references — standard convention, no invented methodology
• ISO 52016-1:2017 — hourly heat balance, energy needs for heating and cooling against fixed setpoints
• CIBSE Guide A — steady-state fabric loss; CIBSE TM41 — degree-days theory and application
• ASHRAE Handbook of Fundamentals — heat balance method, sol-air temperature on opaque surfaces
• EnergyPlus Engineering Reference — Ideal Loads Air System for setpoint-anchored demand
Convention
Heat loss (heating-direction) = U × A × max(0, T_heat_setpoint − T_driving), integrated hourly across the year.
Heat gain (cooling-direction) = U × A × max(0, T_driving − T_cool_setpoint), integrated hourly.
• T_driving = T_sol-air for opaque (walls + roof). Captures hot-air conduction AND solar-absorption-driven conduction.
Sol-air formula: T_sa = T_out + α × G_solar / h_out (ASHRAE/EnergyPlus standard).
• T_driving = T_out for glazing conduction (no sol-air on glass).
• T_driving = T_out for ventilation (no sol-air on air exchange).
Solar transmission through glazing = g_value × G_incident × A, integrated annually. Reported separately from conduction.
Heating demand = max(0, hourly losses − hourly useful gains), summed annually.
Cooling demand = max(0, hourly gains − hourly useful losses), summed annually.
Two independent methods for sanity check
Method 1 — Hourly bottom-up at 21°C setpoint (rigorous):
Raw fabric+vent loss = UA × Σ max(0, 21 − T_out_h) over 8760 hours
Then subtract useful gains explicitly → net heating demand
Method 2 — CIBSE quick estimate via published HDD-15.5 (simplified):
Net heating demand ≈ UA × HDD_15.5 × 24
The 15.5°C cutoff is the outdoor temperature below which typical UK buildings need heat.
Implicitly assumes typical internal+solar gains contribution; not a physics derivation.
Both methods should converge on net heating demand for an approximately typical building.
Tab structure
01_Inputs Single source of truth. Orange cells = editable.
02_Geometry Derived areas and volumes.
03_Compass Building-local facade → true compass bearing.
04_Weather Yeovilton TMYx hourly statistics, baked from EPW.
05_Heat_Loss Per-element heating-direction loss at heating setpoint.
06_Heat_Gain Per-element cooling-direction gain (sol-air opaque) + solar transmission.
07_Internal_Gains People + lighting + equipment + refrigeration.
08_Heat_Balance Losses + gains → heating demand and cooling demand.
09_DHW Bottom-up domestic hot water with editable ASHP/gas split.
10_Ventilation WC extract + MVHR. Fan energy, HRE recovery offsetting heating.
11_Systems VRF/electric heating, VRF/DX cooling. Fuel = demand ÷ efficiency.
12_Other_Loads External lighting, refrigeration, lifts, pumps.
13_Energy_Use Total by fuel. EUI. Carbon emissions.
14_Validation Bottom-up vs measured 2024-25.
Colour coding (matches HIX Static Model)
Orange fill, dark blue text = editable input
Black text = calculation formula
Green text = cross-sheet link to another tab
Grey 9pt = note / source / reference

## 01_Inputs
Bridgewater — Inputs (orange cells editable)
Geometry
| 58.8 | m | Current Bridgewater config
| 14.7 | m
| 5 | - | Ground + 4 above (UK convention)
| 3.2 | m
| 42 | ° | F1 normal at 42° CW from N → NE
WWR per facade (building-local)
WWR F1 (NE) | 0.55 | - | Main facade — bedrooms
WWR F2 (SE) | 0.02 | -
WWR F3 (SW) | 0.12 | - | Bedrooms
WWR F4 (NW) | 0.02 | -
Fabric U-values & sol-air parameters
| 0.18 | W/m²K | cavity_wall_enhanced
| 0.16 | W/m²K | pitched_roof_standard
| 0.22 | W/m²K | ground_floor_slab
| 1.4 | W/m²K | double_low_e
| 0.42 | - | Glazing solar transmittance
| 0.6 | - | Wall solar absorptance (ASHRAE default)
| 0.7 | - | Roof solar absorptance
| 25 | W/m²K | External convection h_out for sol-air
Glazing frame fraction | 0.2 | - | Fraction of glazing area that is frame (no solar transmission)
Setpoints
| 21 | °C | ISO 52016 / CIBSE convention
| 25 | °C
Air infiltration & permanent openings
| 0.2 | ac/h | Background — Q50/20 typical hotel
| 1 | m² | Triple vent louvre
| 0.76 | m² | Triple vent louvre
| 0.13 | ac/h | Equivalent ACH at typical site exposure
| 1.2 | kg/m³
| 1005 | J/kg·K
Internal gains
| 1649271 | person-h/yr | 138 beds × 100% × 8760 h, post-Xmas fix
| 75 | W/person | ISO 7730 seated
| 8 | W/m² | Occupancy sensing
| 4380 | h/yr | 50% diversity
| 15 | W/m² | Small power
| 6000 | h/yr | 68% diversity
| 0.45 | fraction | Useful fraction of gains for offsetting heating
DHW — domestic hot water
| 11500 | m³/yr | Estimated true rate ~32 m³/day
| 0.4 | - | 30-50% range for limited-service hotel
| 10 | °C | UK annual mean cold mains
| 60 | °C | Legionella compliance
| 0.2 | fraction | Pipe + cylinder standing 15-25%
| 0.5 | fraction | ASHP thermal share — editable
| 3 | - | Real-world DHW COP (~35K lift)
| 0.9 | - | Andrews condensing gas heater
| 1500 | kWh/yr | DHW circulation pump
| 1000 | kg/m³
| 4.18 | kJ/kg·K
Mechanical ventilation
| 2292 | L/s | Always-on WC extract
| 0.4 | W/(L/s) | Specific fan power
| 8760 | h/yr
| 1450 | L/s | 5 units × 290 L/s
| 1.4 | W/(L/s) | Combined supply+extract
| 0.8 | - | Sensible recovery efficiency
| 8760 | h/yr
| 0.55 | fraction | Hourly cap fraction — recovery limited by demand
Heating & cooling systems
| 5.12 | - | VRF heat recovery dual-function
| 0.95 | - | Primary
| 1 | - | Electric panel
| 0.05 | - | Secondary
| 3.51 | - | VRF cooling
| 0.95 | - | Primary
| 5.62 | - | DX split secondary
| 0.05 | -
Other electrical loads (annual kWh)
| 8000 | kWh/yr | Walk-in fridge + minibars
| 6000 | kWh/yr | Car park + signage
| 8000 | kWh/yr | 1× hydraulic lift
| 4000 | kWh/yr | Heating + chilled circulation
| 5000 | kWh/yr | Misc plant, controls, BMS
Carbon factors
| 0.207 | kgCO2e/kWh | BEIS 2024 grid average
| 0.183 | kgCO2e/kWh | BEIS 2024 natural gas
Measured energy (Home Office 2024-25 — validation only)
| 560 | MWh/yr
| 200 | MWh/yr

## 02_Geometry
Geometry — derived from inputs
Whole-building
GIA | 4321.8 | m² | Length × Width × Floors
Total height | 16 | m
Volume | 13829.76 | m³
Footprint area | 864.36 | m² | Roof / ground floor area
Facade areas (building-local)
Facade | Total m² | Glazing m² | Opaque m² | WWR | Notes
F1 (building-N → NE) | 940.8 | 517.44 | 423.36 | 55% | Long facade — bedrooms
F2 (building-E → SE) | 235.2 | 4.704 | 230.496 | 2%
F3 (building-S → SW) | 940.8 | 112.896 | 827.904 | 12% | Long facade — bedrooms
F4 (building-W → NW) | 235.2 | 4.704 | 230.496 | 2%
Total | 2352 | 639.744 | 1712.256
Other surfaces
Roof area | 864.36 | m² | Footprint
Ground floor area | 864.36 | m²

## 03_Compass
Compass — building-local to true bearing
Facade bearings (CW from N)
Facade | Local offset ° | True bearing ° | Nearest compass
F1 (building-N) | 0 | 42 | NE
F2 (building-E) | 90 | 132 | SE
F3 (building-S) | 180 | 222 | SW
F4 (building-W) | 270 | 312 | NW
Bridgewater orientation summary
Orientation (CW from N) | 42 | °
With 42° orientation, F1 faces NE, F3 faces SW — matches Yeovilton solar projector

## 04_Weather
Weather — Yeovilton TMYx 2011-2025 (from EPW)
Site & summary
EPW file | GBR_ENG_Yeovilton.AF.038530_TMYx.2011-2025 |  |  | Source: climate.onebuilding.org
Location | Yeovilton AF, Somerset |  |  | 51.006°N, 2.643°W, 22.9m
Annual mean outdoor T | 11.26 | °C |  | From EPW hourly mean
Summer max | 30.2 | °C |  | Annual peak hour
Winter min | -6.8 | °C |  | Annual min hour
Mean wind speed | 3.93 | m/s
Heating Degree Days (published convention)
HDD-15.5 from EPW daily-mean method. Published UK convention metric.
HDD base 15.5°C (annual) | 1736 | K·day/yr |  | Sum of (15.5 − T_out_daily_mean) when positive
HDD base 18.5°C (annual) | 2683 | K·day/yr
Hourly heating temperature integral against 21°C setpoint | 86328 | K·h/yr |  | Σ max(0, 21 − T_out_h) over 8760 hours
Hourly cooling temperature integral against 25°C setpoint | 227 | K·h/yr |  | Σ max(0, T_out_h − 25) over 8760 hours
Ground temperature (annual mean proxy) | 11.26 | °C
Hourly ground floor integral (21°C setpoint − ground T) | 85322 | K·h/yr |  | (21 − 11.26) × 8760, ground assumed at annual mean
Solar — annual incident per surface (kWh/m²/yr)
Surface | Annual incident kWh/m² | Notes
F1 (NE) | 444.4 | kWh/m² |  | Building-local north, faces NE
F2 (SE) | 801.7 | kWh/m² |  | Building-local east, faces SE
F3 (SW) | 879.2 | kWh/m² |  | Building-local south, faces SW — peak
F4 (NW) | 519.5 | kWh/m² |  | Building-local west, faces NW
Roof (horizontal) | 1074.5 | kWh/m² |  | Global horizontal
Sol-air integrals (precomputed from EPW + facade solar)
Hourly Σ max(0, 21 − T_sa_h) for heating, Σ max(0, T_sa_h − 25) for cooling. K·h/yr.
Surface | Heating integral K·h/yr | Cooling integral K·h/yr | Notes
F1 (NE wall, α=0.6) | 77801 | 841 | K·h/yr
F2 (SE wall, α=0.6) | 72588 | 2548 | K·h/yr
F3 (SW wall, α=0.6) | 73133 | 4208 | K·h/yr
F4 (NW wall, α=0.6) | 78059 | 2132 | K·h/yr
Roof (horizontal, α=0.7) | 70772 | 9258 | K·h/yr | Largest cooling-direction integral

## 05_Heat_Loss
Heat loss — heating-direction at 21°C setpoint
Heat loss = U × A × hourly_integral / 1000 (kWh/yr). Sol-air for opaque, T_out for glazing & ventilation.
Fabric — opaque (sol-air convention)
Element | U W/m²K | Area m² | K·h/yr | kWh/yr | MWh/yr | Notes
External wall F1 (NE) | 0.18 | 423.36 | 77801 | 5928.8096 | 5.9288 | Sol-air on opaque
External wall F2 (SE) | 0.18 | 230.496 | 72588 | 3011.6239 | 3.0116 | Sol-air on opaque
External wall F3 (SW) | 0.18 | 827.904 | 73133 | 10898.4786 | 10.8985 | Sol-air on opaque
External wall F4 (NW) | 0.18 | 230.496 | 78059 | 3238.6117 | 3.2386 | Sol-air on opaque
Roof | 0.16 | 864.36 | 70772 | 9787.5977 | 9.7876 | Sol-air on opaque
Fabric — glazing (T_out convention)
Element | U W/m²K | Area m² | K·h/yr | kWh/yr | MWh/yr | Notes
Glazing F1 | 1.4 | 517.44 | 86328 | 62537.3844 | 62.5374 | No sol-air on glass
Glazing F2 | 1.4 | 4.704 | 86328 | 568.5217 | 0.56852 | No sol-air on glass
Glazing F3 | 1.4 | 112.896 | 86328 | 13644.5202 | 13.6445 | No sol-air on glass
Glazing F4 | 1.4 | 4.704 | 86328 | 568.5217 | 0.56852 | No sol-air on glass
Ground floor (ground T convention)
Ground floor | 0.22 | 864.36 | 85322 | 16224.7633 | 16.2248 | Constant ground T (annual mean)
Ventilation (T_out convention)
Source | UA W/K | — | K·h/yr | kWh/yr | MWh/yr | Notes
Background infiltration | 926.5939 | — | 86328 | 79990.9999 | 79.991 | ACH × Vol × ρ × Cp / 3600
Permanent vents (NE+SW louvres) | 602.286 | — | 86328 | 51994.15 | 51.9941 | Equivalent ACH at louvre exposure
Total heat loss
TOTAL fabric + ventilation loss at 21°C setpoint |  |  |  | 258393.9827 | 258.394 | Raw envelope loss before gains credit
Sanity check — CIBSE simplified method
UA × HDD-15.5 × 24 — rule-of-thumb estimate of NET heating demand for typical building.
Differs from gross loss above because 15.5°C cutoff implicitly includes typical gains contribution.
UA total | 3061.1844 | W/K
CIBSE quick estimate = UA × HDD-15.5 × 24 |  |  |  | 127541.1888 | 127.5412 | Sanity check only — net demand estimate

## 06_Heat_Gain
Heat gain — cooling-direction at 25°C setpoint + solar transmission
Heat gain = U × A × hourly_integral / 1000 (kWh/yr). Sol-air for opaque. Glazing solar transmission separate.
Fabric — opaque cooling-direction (sol-air)
Element | U W/m²K | Area m² | K·h/yr | kWh/yr | MWh/yr | Notes
External wall F1 (sol-air) | 0.18 | 423.36 | 841 | 64.0882 | 0.064088
External wall F2 (sol-air) | 0.18 | 230.496 | 2548 | 105.7147 | 0.10571
External wall F3 (sol-air) | 0.18 | 827.904 | 4208 | 627.0876 | 0.62709
External wall F4 (sol-air) | 0.18 | 230.496 | 2132 | 88.4551 | 0.088455
Roof (sol-air) | 0.16 | 864.36 | 9258 | 1280.3592 | 1.2804
Glazing conduction (T_out convention)
Element | U W/m²K | Area m² | K·h/yr | kWh/yr | MWh/yr | Notes
Glazing F1 (conduction) | 1.4 | 517.44 | 227 | 164.4424 | 0.16444
Glazing F2 (conduction) | 1.4 | 4.704 | 227 | 1.4949 | 0.0014949
Glazing F3 (conduction) | 1.4 | 112.896 | 227 | 35.8783 | 0.035878
Glazing F4 (conduction) | 1.4 | 4.704 | 227 | 1.4949 | 0.0014949
Solar transmission through glazing (g × G × A)
Facade | g-value | Glazing m² | Solar kWh/m² | kWh/yr | MWh/yr | Notes
Solar transmission F1 | 0.42 | 517.44 | 444.4 | 77263.3129 | 77.2633 | Always-on, integrated annually
Solar transmission F2 | 0.42 | 4.704 | 801.7 | 1267.1221 | 1.2671 | Always-on, integrated annually
Solar transmission F3 | 0.42 | 112.896 | 879.2 | 33350.7428 | 33.3507 | Always-on, integrated annually
Solar transmission F4 | 0.42 | 4.704 | 519.5 | 821.0926 | 0.82109 | Always-on, integrated annually
Ventilation (T_out convention)
Ventilation cooling gain (infil + perm) | 1528.88 | W/K | 227 | 347.0558 | 0.34706
Totals
Total opaque cooling-direction conduction (sol-air) |  |  |  | 2165.7049 | 2.1657
Total glazing conduction (cooling-direction) |  |  |  | 203.3106 | 0.20331
Total solar transmission through glazing (always-on) |  |  |  | 112702.2705 | 112.7023
Total ventilation cooling-direction gain |  |  |  | 347.0558 | 0.34706
GRAND TOTAL fabric+vent cooling gain at 25°C setpoint (excl. solar transmission) |  |  |  | 2716.0712 | 2.7161 | Plus solar transmission acts as cooling gain when zone above setpoint
Solar through glazing — usefulness split (option c hourly net balance)
Per-hour net balance via option (c). Beneficial = offsets heating demand. Cooling = pushes net balance into cooling-positive. Shoulder = neither.
Facade | Total kWh | Beneficial kWh | Cooling kWh | Shoulder kWh | Beneficial % | Notes
Solar split F1 | 77266 | 17463 | 37662 | 22142 | 22.6% | NE — largest glazing area (517 m²), low direct-sun fraction
Solar split F2 | 1267 | 385 | 541 | 341 | 30.39% | SE — small glazing (5 m²)
Solar split F3 | 33352 | 8472 | 16145 | 8734 | 25.4% | SW — best solar potential per m², small area (113 m²)
Solar split F4 | 821 | 176 | 431 | 214 | 21.44% | NW — small glazing (5 m²)
TOTAL | 112706 | 26496 | 54779 | 31431 | 23.51%
Static values above (not formulas) — precomputed from EPW via option (c) hourly net balance. Same EPW the engine uses. To re-run for different setpoints/fabric, re-run /tmp/_solar_split.py.

## 07_Internal_Gains
Internal gains — heat into zone from occupants, lighting, equipment
Annual internal gains by source
Source | Sensible W | Hours h/yr | kWh/yr | MWh/yr | Notes
People (occupants) | 75 | 1649271 | 108438 | 108.438 | Engine State 2 integration with 1.5/room canonical density
Lighting | 34574.4 | 4380 | 38268 | 38.268 | Engine State 2 integration, current LPD 1.5 W/m² (flagged for BRUKL ingestion)
Equipment (small power) | 64827 | 6000 | 39432 | 39.432 | Engine State 2 integration, current EPD 1.5 W/m² peak (flagged)
Refrigeration waste heat | — | — | 8000 | 8 | Total electric input becomes heat in space eventually
DHW distribution losses (contribute to internal gain) |  |  | 53411.1111 | 53.4111 | Pipe + cylinder losses → space heat
TOTAL internal gains |  |  | 247549.1111 | 247.5491
Useful gain fraction for heating offset
Not all gains usefully offset heating — utilisation factor accounts for timing mismatch.
Useful fraction (heating season) | 0.45 | fraction |  |  | ISO 13790-style; default 0.45
Useful internal gains for heating offset |  |  | 111397.1 | 111.3971
Useful solar gains for heating offset |  |  | 39445.7947 | 39.4458 | ~35% of annual solar is heating-season useful

## 08_Heat_Balance
Heat balance — losses vs gains → heating + cooling demand
Heating-direction balance (against 21°C setpoint)
Component | kWh/yr | MWh/yr | % of loss | Notes
Total fabric + vent heat loss (raw) | 258393.9827 | 258.394 |  | From 05_Heat_Loss
Less: useful internal gains | 111397.1 | 111.3971 | 43.11%
Less: useful solar gains | 26496 | 26.496 | 10.25%
Less: MVHR heat recovery (effective) | 66423.1804 | 66.4232 | 25.71% | Hourly cap × HRE — from 10_Ventilation
NET HEATING DEMAND | 54077.7023 | 54.0777
Cooling-direction balance (against 25°C setpoint)
Component | kWh/yr | MWh/yr | Share | Notes
Fabric + vent cooling gain (sol-air, conduction) | 2716.0712 | 2.7161
Solar transmission through glazing (cooling-season fraction) | 54779 | 54.779 |  | ~45% of annual solar lands when zone above cooling setpoint
Internal gains during cooling hours | 136152.0111 | 136.152
NET COOLING DEMAND | 193647.0824 | 193.6471
Sanity check — CIBSE quick estimate vs bottom-up
Bottom-up net heating demand (above) | 54077.7023 | 54.0777
CIBSE quick estimate (UA × HDD-15.5 × 24) | 127541.1888 | 127.5412 |  | Rule-of-thumb, implicit gains in 15.5°C cutoff
Δ (bottom-up vs CIBSE) | -73463.4865 |  |  | Should be small for typical building; large delta = atypical gain profile

## 09_DHW
Domestic hot water — bottom-up by system
Step 1 — Thermal demand from water volume
Total water consumption | 11500 | m³/yr
Hot water fraction | 0.4 | -
Hot water volume | 4600 | m³/yr
Hot water mass | 4600000 | kg/yr
Temperature lift (cold → delivery) | 50 | °C
Gross thermal demand | 267055.5556 | kWh/yr
Distribution + standing losses | 53411.1111 | kWh/yr |  | 53411.1111 | Pipe + cylinder; contributes back to internal gain
Total thermal input needed | 320466.6667 | kWh/yr
Step 2 — Energy by system (editable ASHP/gas split)
Component | Share | Thermal kWh/yr | Efficiency | Fuel kWh/yr | Notes
ASHP (electric) | 50% | 160233.3333 | 3 | 53411.1111 | Toshiba R32 hybrid pre-heat
Gas heater | 50% | 160233.3333 | 0.9 | 178037.037 | Andrews condensing top-up
DHW circulation pump (electric) | — | — | — | 1500 | Continuous low-power
Total DHW electricity (ASHP + pump) |  |  |  | 54911.1111
Total DHW gas |  |  |  | 178037.037
Check vs measured gas (200 MWh) |  |  |  | 178.037 | Measured gas ~200 MWh; if close → split is consistent

## 10_Ventilation
Mechanical ventilation — fans + heat recovery
Fan electrical energy
System | Flow L/s | SFP W/(L/s) | Hours h/yr | kWh/yr | Notes
WC extract fan (no HR) | 2292 | 0.4 | 8760 | 8031.168
MVHR fan | 1450 | 1.4 | 8760 | 17782.8
Total fan electricity |  |  |  | 25813.968
MVHR heat recovery (sensible)
Component | Value | Units | kWh/yr | MWh/yr | Notes
MVHR mass flow rate | 1.74 | kg/s
Theoretical max recovery (HRE × m_dot × Cp × ΔT_integral) |  |  | 120769.4189 | 120.7694 | If unlimited heating demand to recover into
Effective recovery (capped by heating need per hour) |  |  | 66423.1804 | 66423.1804 | Brief 28j-style hourly cap

## 11_Systems
Heating & cooling systems — fuel from demand
Space heating
System | Share | Thermal kWh/yr | Efficiency | Fuel kWh/yr | Notes
VRF heating (primary, electric) | 95% | 51373.8172 | 5.12 | 10033.9487
Electric panel (secondary) | 5% | 2703.8851 | 1 | 2703.8851
Total heating electricity |  |  |  | 12737.8338
Space cooling
System | Share | Thermal kWh/yr | Efficiency | Fuel kWh/yr | Notes
VRF cooling (primary) | 95% | 183964.7282 | 3.51 | 52411.6035
DX split (secondary) | 5% | 9682.3541 | 5.62 | 1722.8388
Total cooling electricity |  |  |  | 54134.4423

## 12_Other_Loads
Other electrical loads — refrigeration, lighting, lifts, pumps
Annual electrical consumption
Load | kWh/yr | MWh/yr | Notes
Lighting (internal) | 151435.872 | 151.4359 | From 07_Internal_Gains
Equipment (small power) | 388962 | 388.962 | From 07_Internal_Gains
Refrigeration | 8000 | 8 | Walk-in fridge + minibars
External lighting | 6000 | 6 | Car park + signage
Lifts | 8000 | 8 | 1× hydraulic
Pumps | 4000 | 4 | Heating + chilled circulation
Other miscellaneous | 5000 | 5 | BMS, controls, plant
Total other loads | 571397.872 | 571.3979

## 13_Energy_Use
Total energy use — by fuel, EUI, carbon
Electricity — by end use
End use | kWh/yr | MWh/yr | % of elec | Notes
Space heating (VRF + panel) | 12737.8338 | 12.7378 | 1.772%
Space cooling (VRF + DX) | 54134.4423 | 54.1344 | 7.529%
DHW (ASHP + pump) | 54911.1111 | 54.9111 | 7.637%
Ventilation fans | 25813.968 | 25.814 | 3.59%
Lighting (internal) | 151435.872 | 151.4359 | 21.06%
Equipment (small power) | 388962 | 388.962 | 54.1%
Refrigeration | 8000 | 8 | 1.113%
External lighting | 6000 | 6 | 0.8345%
Lifts | 8000 | 8 | 1.113%
Pumps (non-DHW) | 4000 | 4 | 0.5563%
Other (BMS, controls) | 5000 | 5 | 0.6954%
TOTAL ELECTRICITY | 718995.2272 | 718.9952
Gas — by end use
End use | kWh/yr | MWh/yr | % of gas | Notes
DHW (gas heater) | 178037.037 | 178.037 | 100%
TOTAL GAS | 178037.037 | 178.037
Summary — total, EUI, carbon
Metric | Value | Units |  | Notes
Total electricity | 718.9952 | MWh/yr
Total gas | 178.037 | MWh/yr
Total site energy | 897.0323 | MWh/yr
EUI (per m² GIA) | 207.5599 | kWh/m²
Carbon — electricity | 148.832 | t CO2e/yr
Carbon — gas | 32.5808 | t CO2e/yr
Total carbon | 181.4128 | t CO2e/yr
Carbon intensity per m² GIA | 41.9762 | kgCO2e/m²

## 14_Validation
Validation — bottom-up vs measured
Bottom-up vs measured (Home Office 2024-25)
Metric | Bottom-up | Measured | Δ | Δ % | PASS/FAIL ±15%
Electricity MWh/yr | 718.9952 | 560 | 158.9952 | 28.39% | FAIL
Gas MWh/yr | 178.037 | 200 | -21.963 | -10.98% | PASS
EUI kWh/m² | 207.5599 | 175.8527 | 31.7072 | 18.03% | FAIL
Per-component sanity checks
Component | Bottom-up MWh/yr | Notes
Total fabric+vent heat loss (gross) | 258.394 |  |  |  | Validation target for Brief 28k engine fix
Net heating demand (after gains) | 54.0777
Net cooling demand | 193.6471
CIBSE quick estimate (UA × HDD-15.5 × 24) | 127.5412 |  |  |  | Rule-of-thumb sanity check on net heating demand